## LLFA Comments
Item | Information | Stantec Response | Further Work Required | Stantec Response
1. The Full Drainage Strategy which uses the appropriate and consistent design parameters across all aspects of the design to ensure the surface water runoff and has an adequately sized attenuation that complies with National Standards and local guidance. | Informative - The LLFA observes there is no mention of the LLFA's Developer Guidance in section 1 of the FRA. It is not clear whether the applicant has considered this guidance in accordance with the NPPF paragraph 175. This becomes clearer in section 7, where in section 7.2.4 there is no mention of the LLFA's support for the OFWAT Sewer Sector DCG approach to require rainwater reuse as a first option. | The LLFA's Developer Guidance document is now referenced to in Section 1 of the FRA. A new paragraph (7.2.5), has been written to present the DCG Drainage Hierarchy. | The design calculations have been undertaken with both FEH13 and FSR. The FSR results have been used for the 15 and 30 minute storm duration event and then FEH13 for the 60-5760 minute event. It is not clear to the LLFA why this approach has been applied as InfoDrainage is capable of running calculations for the 15 and 30 minute storm events. It is not possible to make any comparison of the submitted information to demonstrate the suitability of one method over the other. Furthermore, the LLFA note that in the FEH set of results that have been sorted by critical storm duration, the results identified for each feature have identified the small duration summer storm events as the critical storms. Therefore, it is possible that the 15 and 30 minute storm durations could be the critical storm duration. the LLFA would expect either further robust justification for this approach or to undertake the calculations using the FEH13 method. Further work required. | The rainfall data used in the InfoDrainage model simulations has now been revised to FEH13 for the 15-5760 minute events, in accrordance with the LLFA's Developer Guidance.
| Informative - In section 4 of the FRA, the climate change allowances are given for the 1% AEP event in Table 4-1 which are appropriate. Although, there is no consideration for the 3.3% AEP event allowances in this section, there is the application of the 40% allowance to the 3.3% AEP event in the hydraulic modelling scenario (see section 7.3.22). This is supported by the parameters shown in the surface water Drainage calculations (page 19/56 in Appendix E InfoDrainage Calculations). | The climate change allowances in Table 4-1 have been updated to show allowances for the 3.3% AEP event for the Broadland Rivers Management Catchment.
2. Contradictions in the design information and the design calculations are solved; | The infiltration testing results are presented in Appendix H (not appendix G as reported in the FRA). In section 7.3.17 of the FRA it is stated that "The median design rate of these three tests is 0.212m/hr, which is used to model the infiltration swale". Rather than following the LLFA's developer guidance that requires lowest rate of infiltration to be used (see section 12.8 which states "The lowest value obtained across the site, or across representative geology, to be used for calculations." The same approach was indicated to have been applied to the south-eastern infiltration basin (see section 7.3.19).On further inspection of the infiltration testing results, the infiltration rate for the basin on the south-eastern boundary has an infiltration rate of 0.126 m/hr applied which is considered to be the lowest rate. However, the infiltration swale on the north-eastern boundary of the site is shown to have applied the median rate of 0.212 m/hr rather than the lowest rate of 0.011 m/hr. The LLFA will require the calculations to be updated with the lowest rate of infiltration rather than the median. | The lowest infiltration rate has been applied for the infiltration basin design (TP04). The median infiltration rate is applied for the infiltration swale design (TP03) as the lowest infiltration rate is not consistent with the surrounding soil testing and, therefore, considered to be anomalous. Text has been added to section 7.6 in the FRA to this affect. Also, the soil testing data is presented in Appendix G to show layout of infiltration testing. | A review of the design calculations has highlighted inconsistencies with the parameters used in the hydraulic modelling for the infiltration basin along the south-east boundary. For example, the exceedance level in the calculation (page 10/56) is stated as 89.150m, while the drawings shows a level of 89.2m. This means there is a difference also in the basin depth of 50mm and will also alter the top area. The side slope is stated in the calculations as 1:1.74 while in the FRA report in section 7.3.11 it is stated as 1:2.5. All these variations alter the storage volume associated with the infiltration basin and impacts on whether the basin capacity is suitable for use. It also means the modelled calculations do not represent what is proposed to be built. A similar issue has been identified in the parameters used for the infiltration swale, where the exceedance level in the calculation (page 14/56) is stated as 89.135m, while the drawings shows a level of 89.2m. This means there is a difference also in the basin depth which is stated as 400mm on the drawing and in the modelling calculations resulting in differing base levels in the drawing and the modelling calculations. Again, this will also alter the top area given in the calculations. The median infiltration rate has been applied in the calculations rather than the lowest rate (further information is given on this point below). Further work is required, as it is not possible to confirm whether the calculations represent the proposed design in the submitted FRA report and supporting design drawings. Further work required. | The discrepancies discussed in this section have now been addressed in the report and on the drawings. For clarity the following values are used. The infiltration basin exceedance level is 89.164m AOD measured to the back of the gabion basket headwall. The proposed gradient of the infiltration varies - 1:2.5 along western bank, near-vertical on soil-retained eastern bank, and 1:3 at northern and southern ends. As InfoDrainage models a single gradient, an average gradient of 1:1.74 is shown in the InfoDrainage model. The top area of 270.06m2 and base area of 82.94m2 are consistent between the InfoDrainage model and design layout. Commentary has been added to this effect in paragraph 7.5.4. The Infiltration swale overflow level is 89.224m AOD, and has been revised on drawing 49868_2001_521 and the InfoDrainage calculations.
| Informative - In addition, the trial pit depths for pits 07 and 08 on the south-eastern infiltration basin are 2.9m and 3m depth respectively. The proposed basin design depth is shown as 1.35m to the bed of the basin on the drawings and is stated as 1.3m deep in section 7.3.12 in the FRA. However, the subbase is a further 0.8m deep below the base of the basin. This means the total depth of the structure is 2.15m. This is not a similar depth as the infiltration tests for this location. The application of the worst infiltration rate should be applied as a precautionary approach. | Borehole logs from the 2022 testing in trial pits TP07 and TP08 show a homogenous layer of Britons Lane SAND and Gravel for depths of 0.3 - 2.9m (TP07), and 0.3 - 3m (TP08). Therefore, the testing is representative for the design depth of 2.115m. Text has been added to this effect in paragraph 7.6.9. | Currently, the calculations for the proposed surface water drainage indicate that in a 1% AEP plus 45% climate change event, the Infiltration swale is shown to have a flooded volume of 4.203 m3 (page 22/56 in the drainage calculations). This is with the median infiltration rate for the swale's design rather than the required lowest infiltration rate. Therefore, it is considered possible that the application of the lowest infiltration rate to the proposed design calculations would see an increased surface water volume. Further work required. | Recent design adjustments have lead to a higher infiltration swale flood volume of 10.184m3. The proposed site levels direct this flooding into the infiltration basin which has capacity for the additional 10.184m3 whilst maintaining a freeboard of 300mm.
|  |  | On review of the construction details drawing (Drawing number: 49868/2001/521) it appears the water level in the infiltration swale for the 1% AEP plus 45% climate change allowance appears to be at a similar level to the ground level at the top of the basin. On review of the ground levels shown on the Flood Exceedance Plan (Drawing Number 49868/2001/530), it is clear that the top of bank levels for the infiltration feature varies from approximately 89.9m in the northern extent of the swale to be between 89.2m and 89.3m at the southern extent of the basin. The 1% AEP plus 45% climate change allowance water level shown on the drawing (drawing number: 49868_2001_521 Rev P07) is 89.217m with a top of bank level shown as 89.2m. Therefore, the drawings currently demonstrate that the water level is higher than the designed top of bank level of the basin. The LLFA notes the supporting calculations also show the swale floods in the 1% AEP plus 45% climate change allowance event. The LLFA requires that further consideration to the ground levels for this basin is undertaken. Further work required. | The flood levels in the swale are 89.314m AOD and 89.427m AOD for the the 3.3% AEP event +CC and the 1% AEP event +CC, respectively. Although these levels are above the basin containment level of 89.164m AOD, flood water will not over-top the basin because the site levels direct the flood water from the swale into the basin and flood volume is small enough to be stored in the basin (3.856m3 and 10.184m3 for the 3.3% AEP event +CC and 1% AEP +CC).
|  |  | The raingarden design has only one point of concern, which relates to the levels of the down pipe indicated but not confirmed in Construction Details drawing (drawing number: 49868-2001-521 P07). The downpipe discharging into the Rain Garden is shown to be below the water level of the 1% AEP plus 45% climate change event. This would cause water in the down pipe to potential prevent water discharging into the feature and surcharge in the downpipe. The LLFA would recommend the down pipe outfall is raised up to above the 1% AEP plus 45% climate change event level to prevent this matter from occurring. Further work required. | Downpipe detail has been ammended on drawing 49868-2001-521 with the outlet now above the maximum design water level. The detail has been progressed to show a watering can style discharge without the nozzle to avoid clogging. The inlet area is designed to dissipate flows from the watering can to avoid erosion in the bio-retention area.
3. That all information contained in the drawings provided is finalised to ensure an adequate demonstration that the development is in accordance with the National Planning Policy Framework (NPPF) and the LLFA’s Developer Guidance with regard to the risk of flooding. | There are a number of design details that are in abeyance bubbles on the Construction details drawing (drawing number: 49868_2001_521 Rev P07). These un-confirmed design aspects relate to the design of the attenuation basin on the | These bubbles were to indicate drawing revision changes rather than in abeyance design. The all bubbles have been removed from drawings to avoid confusion. | Exceedance Flow Route Plan does not contain the finished floor levels (FFL) of the proposed buildings. These FFLs need to be included for the plan to be complete. In addition, there may be changes to the proposed design due to the need for design updates. Further work required. | Finished floor levels have now been added to the Exceedance Flow Route Plan - drawing 49868_2001_530.
|  |  | Maintenance and management plan is provided but there is no mention of the gabion basket structure in the maintenance plan. As the condition of this structure could affect the performance of the infiltration basin should it fail, the LLFA request that consideration of this structure is included in the maintenance and management plan. Further work requested. | Considerations for the maintennce and management of the gabion baskets have been added to Table 7-13.
|  |  | infiltration basin on the south eastern boundary and the infiltration basin on the north-eastern boundary. Information such as pipe gradients, pipe diameters, attenuation tank size and material selection are yet to be confirmed. The LLFA require this information at detail design at full planning application stage. Furthermore, on the catchment area plan (drawing number: 49868/2001/503 P05), there is an in-abeyance bubble around catchment CA_11. Therefore, it is not confirmed to which discreet drainage area this sub-catchment will be draining to and ultimately affects the accuracy of the surface water drainage design calculations. In addition, the proposed drainage layout (drawing number: 49868/2001/501 P08) is shown to have in abeyance bubbles around "v septor" and associated "penstock value" on the south-eastern infiltration basin and the details for the washout point and air vent on the geo-celluar storage feature. There is also a bubble around the foul drainage cesspool, but this is not a matter the LLFA advises on. Further work required to confirm these relevant details. | These bubbles were to indicate drawing revision changes rather than in abeyance design. The all bubbles have been removed from drawings to avoid confusion.
Further guidance on the information required by the LLFA from applicants can be found at: https://www.norfolk.gov.uk/rubbish-recycling-and-planning/flood-and-water-management/information-for-developers